## Boundary conditions
Type | Parameter | Value | Unit | Notes
Weather | Location | Hourly temp, wind, solar | - | TMY, EPW Data
Demands | Electricity | Hourly demand profile | kW
| Heat | Hourly demand profile | kW
| Cooling | 0 | kW
| Hydrogen | 0 | kW
Technical Boundary Conditions: Photovoltaics | Min. Area | 0 | m2
| Max. Area |  | m2 | The local limit for max. area
| Efficiency | 18 | %
| Investment unit cost | 850 | €/kWp
| Service life | 20 | a
| Operating costs | 2 | % Investment
Technical Boundary Conditions: Wind turbine | Min. Capacity | 0 | kWel
| Max. Capacity |  | kWel | The local limit for wind resource
| Hellmann Coefficient | 0.14 | -
| Hight of Wind turbine | 122 | m
| Ref. Hight for wind speed | 10 | m | The hight of measure point
| Investment unit cost | 1300 | €/kW
| Service life | 20 | a
| Operating costs | 3 | % Investment
Technical Boundary Conditions: CHP | Min. Capacity | 0 | kWel
| Max. Capacity | 10000 | kWel
| El. Efficiency | 38 | %
| Th. Efficiency | 52 | %
| Investment unit cost | 1100 | €/kWel
| Service life | 15 | a
| Operating costs | 8 | % Investment
Technical Boundary Conditions: Boiler | Min. Capacity | 0 | kWth
| Max. Capacity | 10000 | kWth
| Efficiency | 92 | %
| Investment unit cost | 100 | €/kWth
| Service life | 20 | a
| Operating costs | 3 | % Investment
Technical Boundary Conditions: Heat Pumpe | Min. Capacity | 0 | kWth
| Max. Capacity | 10000 | kWth
| COP | 4 | - | Could set to variable accroding to air temperatur
| Investment unit cost | 900 | €/kWth
| Service life | 18 | a
| Operating costs | 2.5 | % Investment
Technical Boundary Conditions: Electro Boiler | Min. Capacity | 0 | kWth
| Max. Capacity | 10000 | kWth
| Efficiency | 98 | %
| Investment unit cost | 80 | €/kWth
| Service life | 20 | a
| Operating costs | 1 | % Investment
Technical Boundary Conditions: Comperssion Chiller | Min. Capacity | 0 | kWth
| Max. Capacity | 10000 | kWth
| EER | 5 | -
| Investment unit cost | 600 | €/kWth
| Service life | 15 | a
| Operating costs | 3.5 | % Investment
Technical Boundary Conditions: Absorption Chiller | Min. Capacity | 0 | kWth
| Max. Capacity | 10000 | kWth
| Efficiency | 60 | %
| Investment unit cost | 600 | €/kWth
| Service life | 18 | a
| Operating costs | 3 | % Investment
Technical Boundary Conditions: Thermal Energy Storage (Heat) | min. volume | 0 | m3
| max.volume | 1000 | m3
| Temperature spread | 40 | K
| Storage losses | 0.2 | %/h
| Investment costs | 640 | €/m3
| Service life | 20 | a
| Operating costs | 2 | % Investment
Technical Boundary Conditions: Thermal Energy Storage (Cold) | min. volume | 0 | m3 | Only for water storage. PCM not considered
| max.volume | 1000 | m3
| Temperature spread | 15 | K
| Storage losses | 0.2 | %/h
| Investment costs | 640 | €/m3
| Service life | 20 | a
| Operating costs | 2 | % Investment
Technical Boundary Conditions: Battery | Min. capacity | 0 | kWh
| Max. Capacity | 10000 | kWh
| Standby losses | 0.1 | %/h
| Investment costs | 850 | €/kWh
| Service life | 10 | a
| Operating costs | 1 | % Investment
Economic boundary conditions | Electricity price | 0.21 | €/kWh | 0.21(with HP tax) 0.26(other elaectircity)
| Electricity Feed-in tariff | 0.09 | €/kWh
| Limitation electricity from grid | - | MWh/a
| Gas price | 0.043 | €/kWh
| Limitation gas from grid | - | MWh/a
| Biogas costs | 0.08 | €/kWh | Not considered. if neccesary, could be added into model
| Interest rate | 5 | %
| Year of consideration | 20 | a
Ecological boundary conditions | CO2 price | 31.6 | €/tCO2
| CO2 Emission for Electricity | 410 | g/kWh
| CO2 Emission for Gas | 200 | g/kWh
| CO2 Emission for Biogas | 107 | g/kWh

## weather description
姓名 | 单元 | 描述 | 数据更新频率
temp_dry | °C | Present air temperature measured 2 m over terrain | 10 min
temp_dew | °C | Present dew point temperature measured 2 m over terrain | 10 min
temp_mean_past1h | °C | Latest hour's mean air temperature measured 2 m over terrain | Hourly
temp_max_past1h | °C | Latest hour's maximum air temperature measured 2 m over terrain | Hourly
temp_min_past1h | °C | Latest hour's minimum air temperature measured 2 m over terrain | Hourly
temp_max_past12h | °C | Last 12 hours maximum air temperature measured 2 m above ground. Measured at 0600 and 1800 UTC. | Twice a day
temp_min_past12h | °C | Last 12 hours minimum air temperature measured 2 m above ground. Measured at 0600 and 1800 UTC. | Twice a day
temp_grass | °C | Present air temperature measured at grass height (5-20 cm over terrain) | 10 min
temp_grass_max_past1h | °C | Latest hour's maximum air temperature measured at grass height (5-20 cm over terrain) | Hourly
temp_grass_mean_past1h | °C | Latest hour's mean air temperature measured at grass height (5-20 cm over terrain) | Hourly
temp_grass_min_past1h | °C | Latest hour's minimum air temperature measured at grass height (5-20 cm over terrain) | Hourly
temp_soil | °C | Present temperature measured at a depth of 10 cm | 10 min
temp_soil_max_past1h | °C | Latest hour's maximum temperature measured at a depth of 10 cm | Hourly
temp_soil_mean_past1h | °C | Latest hour's mean temperature measured at a depth of 10 cm | Hourly
temp_soil_min_past1h | °C | Latest hour's minimum temperature measured at a depth of 10 cm | Hourly
humidity | % | Present relative humidity measured 2 m over terrain | 10 min
humidity_past1h | % | Latest hour's mean for relative humidity measured 2 m over terrain | Hourly
pressure | hPa | Atmospheric pressure at station level | 10 min
pressure_at_sea | hPa | Atmospheric pressure reduced to mean sea level | 10 min
wind_dir | degree | Latest 10 minutes' mean wind direction measured 10 m over terrain. 0 means calm | 10 min
wind_dir_past1h | degree | Latest hour's mean wind direction measured 10 m over terrain | Hourly
wind_speed | m/s | Latest 10 minutes' mean wind speed measured 10 m over terrain | 10 min
wind_speed_past1h | m/s | Latest hour's mean wind speed measured 10 m over terrain | Hourly
wind_gust_always_past1h | m/s | Latest hour's highest 3 seconds mean wind speed measured 10 m over terrain | Hourly
wind_max | m/s | Latest 10 minutes' highest 3 seconds mean wind speed measured 10 m over terrain | 10 min
wind_min_past1h | m/s | Latest hours lowest 3 second mean wind speed measured 10 m over terrain | Hourly
wind_min | m/s | Latest 10 minutes' lowest 3 seconds mean wind speed measured 10 m over terrain | 10 min
wind_max_per10min_past1h | m/s | Maximum 10-minute average wind speed in the one hour period preceding the time of observation | Hourly
radia_glob | W/m² | Latest 10 minutes global radiation mean intensity | 10 min
radia_glob_past1h | W/m² | Mean intensity of global radiation in the latest hour | 10 min
sun_last10min_glob | minutes | Number of minutes with sunshine the latest 10 minutes | 10 min
sun_last1h_glob | minutes | Number of minutes with sunshine the latest hour | Hourly
leav_hum_dur_past10min | minutes | Number of minutes with leaf moisture the latest 10 minutes | 10 min
leav_hum_dur_past1h | minutes | Number of minutes with leaf moisture the latest hour | Hourly